Feasibility Study Deliverable Review Standard

The rulebook for first-pass review of consultant submissions

Internal document. Not for circulation to bidders or the Developer's partners in this form. Section 11 sets out what may be shared.

| Field | Detail |
| --- | --- |
| Document | Feasibility Study Deliverable Review Standard (FS-RS), v0.1 draft |
| Owner | Dennis Nderitu, AfCEN |
| Augments | AfCEN CDE Platform PRD. Supplies the content layer for FR-3, FR-4, FR-5, FR-6 and FR-7. |
| Used by | Kwanza PM team, as the first-pass review rulebook. AfCEN platform administrator, to configure the checks. |
| Pilot project | Bulambuli-Moroto IPT Project (RFP-TFS-IPT-BM-002/2026) |
| Reference template | Pre-Feasibility Study for the Proposed 132 kV Bulambuli-Moroto-Kitgum Transmission Project (Phase One), responsAbility Renewable Energy Holding, August 2020, 132 pp. |
| Status | Draft for internal build use. Open items in Sections 9 and 12. |

# 1  Why this document exists

The Platform PRD specifies a mechanism. FR-4 says the system checks the consultant's figures against the benchmark library and flags entries that deviate beyond a configurable threshold. It does not say which figures are checked, what a complete deliverable section must contain, or what a flag means when it fires. FR-3 says the benchmark library holds capex figures and prior project data, but not which metrics.

Without that content layer, FR-4 is a threshold with little to compare against, and first-pass review falls back to a person reading a PDF, which is the problem the platform exists to solve. This standard is the content layer. It states, per deliverable section, what must be present, what must evidence it, and what raises a flag.

It also answers the objection Arnold has already flagged, on its own terms. The standard is what makes the platform faster than manual review: the checks are written down once and run on every submission, in seconds, consistently. It does not review instead of the PM team. Every output is a flag that the PM team accepts or dismisses, and the PM team's judgement is the thing being accelerated.

# 2  Boundaries

These carry over from the Platform PRD unchanged and govern everything below.

- AfCEN's checks are advisory only.

- The Consultant remains the sole signatory of its own deliverables under TOR Section 8.3.

- The Kwanza PM team remains the sole approval authority.

- The standard never auto-corrects or overwrites a submitted figure (FR-5).

- A flag is a question put to the PM team, not a finding against the Consultant.

# 3  Where the standard runs

| CDE state | What the standard does | Who decides |
| --- | --- | --- |
| Work in Progress | Nothing. This is the Consultant's own space. | Consultant |
| On submission to Shared | Runs Part A and the applicable Part B and Part C checks. Generates flags with the reference source shown alongside each one (FR-4). Updates the PM dashboard (FR-6). | No decision is taken |
| Shared, under review | Flags presented with the Consultant's response. PM accepts or dismisses each. | PM team |
| Published | No checks. Entry to Published follows the PM team's approval only. | PM team |

The flag-accepted versus flag-dismissed ratio is the success metric in the Platform PRD. Section 7 explains why the launch configuration should be deliberately conservative to protect it.

# 4  Flag taxonomy

| Severity | Meaning | Default PM action |
| --- | --- | --- |
| Blocking | A required element is absent or carries no evidence, so the section cannot be assessed at all. | Return to the Consultant before review time is spent on it. |
| Material | Present, but deviates from the standard or a benchmark beyond the configured threshold. | Review alongside the Consultant's response. |
| Advisory | Formatting, consistency or traceability. | Batch and clear at the decision gate. |

# 5  Part A. Universal checks

These run on every deliverable, in every section. They are cheap, they are machine-checkable, and they are where a first-pass check earns its keep.

| ID | Check | Severity | Run by |
| --- | --- | --- | --- |
| U-1 | Every quantitative claim carries a source reference. | Blocking | Machine flags absence; PM judges adequacy |
| U-2 | Units are stated and consistent. No non-currency quantity is summed into a currency total. | Blocking | Machine |
| U-3 | Every total recomputes from its stated components. | Blocking | Machine |
| U-4 | Every percentage recomputes from its stated base. | Material | Machine |
| U-5 | Acronyms expanded at first use. | Advisory | Machine |
| U-6 | Figures and tables numbered, titled and sourced. | Advisory | Machine |
| U-7 | Version and revision history present. | Blocking | Machine |
| U-8 | Consultant sign-off present, per TOR Section 8.3. | Blocking | Machine |
| U-9 | A given value is identical wherever it appears across deliverables. | Material | Machine |
| U-10 | Assumptions register updated, each entry classed as measured, modelled or assumed. | Material | Machine flags absence; PM judges the class |

U-2 and U-3 are not hypothetical. Section 8 works a real example from the reference document.

# 6  Part B. Section acceptance criteria

Section numbering follows the reference document, which is the house structure for a transmission study in this programme. The reference is a pre-feasibility study, so for several sections the standard requires depth the reference does not itself demonstrate. Those are marked.

| Section | Must be present | Must be evidenced by | Flag if |
| --- | --- | --- | --- |
| 1 Introduction and background | Project justification against current national and grid development plans. | Plans cited with vintage. | Plan cited is more than one vintage out of date. |
| 2 Project description, demand and supply | Load forecast across scenarios. Load flow, N-1 and stability. Preliminary design: conductor, compensation, transformer ratings, protection. | Contracted or committed demand evidence. Utility network case reference. Grid code clause. | Demand is indicative only. Network model not aligned to the utility case. Conductor still unconfirmed. |
| 3 Description of project area | Final surveyed alignment. Topography, geology, ecology, socio-economics. ESIA and RAP position. | Survey report reference. DTM resolution and date. Borehole logs. Named GIS layers. | Topography from regional data. Foundations not resolved per tower. Protected-area claim with no named layer. |
| 4 Financial and economic parameters | CAPEX and OPEX build-up. EIRR, NPV, BCR. FIRR, DSCR, tariff and payment security. Sensitivities. Financing structure. | Surveyed quantities. Rate basis with date. Model file version. | Cost built from a per-km rule of thumb. No DSCR. Accuracy band absent or wider than target. |
| 5 Stakeholder engagement | Full consultation record and issues log. | Minutes, attendance, issue resolution. | Engagement is scoping-phase only. |
| 6 Legislation, regulations and permits | Permit register with status and owner per permit. | Statute citation. Permit references. | A permit is listed with no status or owner. Protected-area permit missing where the corridor crosses one. |
| 7 Risks and barriers | Quantified risk register. | Likelihood, impact, mitigation and owner per risk. | Register is a narrative list. |
| 8 References | All sources traceable. | Evidence store links. | A reference is not in the evidence store. |
| 9 Implementation schedule | Integrated schedule to commissioning. | Critical path and dependencies. | Schedule not linked to procurement and permits. |
| 10 Governance and structure | Sponsor, SPV, roles. | Executed or draft agreements. | Sponsor undesignated. |
| 11 Climate and resilience | Hazard exposure and design response. | Named hazard dataset. | Absent. |
| 12 Procurement strategy | Packaging and contracting approach. | Rationale against market. | Absent. |
| 13 Readiness assessment | Weighted scorecard, scored per element. | Evidence link per element. | A score with no evidence link. |

Section 4 is where the reference template is thinnest. Its Financial and Economic Parameters section is a single cost table with no IRR, no NPV and no DSCR. That is appropriate at pre-feasibility and unacceptable at feasibility, so it is where this standard does the most work.

# 7  Part C. Benchmark rules

FR-4 needs values to check against. The reference document supplies the first set. Each entry is tagged with source, date and region, as FR-3 requires, and carries a confidence field, which FR-3 does not currently require but should.

| Metric | Value | Source | Date / region | Conf. |
| --- | --- | --- | --- | --- |
| 132 kV double-circuit AAAC240 OHL, supply and erection | 153,846 USD/km | Bulambuli-Moroto PFS, Table 8 | Aug 2020, Uganda | Low |
| 132 kV substation | 5,000,000 USD lump sum | Bulambuli-Moroto PFS, Table 8 | Aug 2020, Uganda | Low |
| Contingency | 10% of OHL plus substation | Bulambuli-Moroto PFS, Table 8 | Aug 2020 | Medium |
| Consultancy services | 5% of OHL plus substation | Bulambuli-Moroto PFS, Table 8 | Aug 2020 | Medium |
| ESIA and RAP studies | 500 USD/km of OHL | Bulambuli-Moroto PFS, Table 8 | Aug 2020, Uganda | Low |
| Land take | 8.65 acres/km, about a 35 m effective corridor | Derived across all three options | Aug 2020, Uganda | Medium |
| Compensation | 1,000 USD/acre | Bulambuli-Moroto PFS, Table 8 | Aug 2020, Uganda | Low |
| 400 kV single-circuit HVAC, total capex | about 1.50 M USD/km | Ghanzi-Gobabis pre-feasibility, 432 M USD over 288.47 km | 2026, Botswana-Namibia | Low |

## 7.1  What this set is, honestly

This is one project plus one adjacent data point. It is a seed, not a benchmark library, and the standard should say so internally rather than let a threshold imply a confidence that is not there. Four specific weaknesses:

- The rates are August 2020 and have not been escalated.

- The per-km rate is flat across all three route options, from 123 km to 152 km. That is a pre-feasibility simplification, so it benchmarks pre-feasibility practice rather than feasibility practice. Real per-km cost varies with terrain, which is precisely what the Mt. Elgon foothills section of this corridor would show.

- The substation figure is identical across all three options, so it is a placeholder rather than a costed design.

- Supply and erection are not separated, so the benchmark cannot isolate a rate movement in either.

Recommendation. Before launch, escalate the 2020 rates to current prices, add at least three comparable projects per metric, and separate supply from erection. Until a metric has three or more sources, a deviation against it should raise an Advisory flag at most, never Material. This is the direct answer to the Platform PRD's own open question about what happens when the reference data is itself outdated or inapplicable: the confidence field decides the maximum severity, and the provenance tags let the PM team dismiss the flag in one look.

# 8  Part D. Worked example, from the reference document

Table 8 of the reference PFS gives a live example of a check that pays for itself, and it is a good candidate for the Saturday demo because it is real, verifiable and already in the data room.

Recomputing Option 1 (152 km) from the table's own components:

| Component | Stated | Check |
| --- | --- | --- |
| OHL supply and erection | 23,384,615 | 153,846 USD/km x 152 km |
| Bulambuli substation | 5,000,000 | lump sum |
| Contingencies 10% | 2,838,461.50 | 10.00% of 28,384,615. Correct. |
| Consultancy services 5% | 1,419,230.75 | 5.00% of 28,384,615. Correct. |
| ESIA and RAP studies | 76,000 | 500 USD/km x 152 km. Correct. |
| Compensation | 1,315,000 | 1,000 USD/acre x 1,315 acres. Correct. |
| Sum of the currency rows | 34,033,307.25 |  |
| Total stated in the table | 34,034,622 | Differs by 1,314.75 |

The difference of 1,314.75 is the row above it: Land requirement in acres, 1,315. The acres figure has been summed into the dollar total. The same holds on the other two options: Option 2 differs by 1,219 against an acres figure of 1,219, and Option 3 differs by 1,064 against an acres figure of 1,064. On all three, adding the acres row to the currency rows reproduces the stated total exactly.

Why this is the right demo flag. It is financially immaterial, about 1,300 USD on 34 M, and that is the point. It is not a judgement about anyone's engineering. It is check U-2, a non-currency quantity summed into a currency total, and check U-3, a total that does not recompute. A machine catches it on submission in milliseconds and shows the source. A reviewer reading a PDF table generally does not, and should not have to. That is the PM-team argument made concretely: the platform takes the arithmetic hygiene so the PM team's time goes to the engineering.

Confirm this against the source table before using it externally. The reconstruction above is from the PDF text layer.

# 9  Deliverable mapping

FR-7 tracks deliverables D1 to D11 against the timing in TOR Section 8.1. That TOR is not in hand here, so the mapping of this standard to each deliverable is left open rather than guessed at. To complete it, list for each of D1 to D11 which Part B sections apply and which Part C benchmarks can fire. An earlier version of the development TOR ran to D1 to D9, so the deliverable set has changed and should be read from the issued document rather than from precedent.

# 10  Cost reconciliation, project-specific

The reference PFS costs the line and substation at 28.6 M to 34.0 M USD depending on route option. Project records indicate a Total Project Cost of about 70.58 M USD in the Developer's Project Cost Model, with a development-phase budget of about 5.76 M USD and an Owner's Advisers envelope of about 1.81 M USD.

These are different scopes rather than a contradiction. The PFS figure is construction scope. The Total Project Cost is the whole project including development, advisers and financing. The standard requires the FS to publish the bridge between them, itemised as surfaced cost against added scope, because that is the first question a lender asks and the gap is large enough to invite it.

Confirm both figures against the Project Cost Model before use. They come from project records rather than from the PFS itself.

# 11  Disclosure

This standard splits cleanly into a layer that benefits from being published and a layer that must not be.

| Layer | Handling |
| --- | --- |
| Part A and Part B | Safe to share with bidders and the Consultant, if the Developer chooses. Telling a consultant what a deliverable must contain raises the quality of what arrives and reduces rework. It also delivers the deliverable-standards idea from the original six proposals without reopening the RFP evaluation criteria, which the 15 July call deferred. |
| Part C | Internal only. The benchmark values, their provenance and their confidence fields are AfCEN's asset. |
| Accumulation across projects | Internal only, per FR-11 and the Platform PRD's own instruction. Externally, if described at all, this is version tracking and quality assurance. |

One tension worth naming. Publishing Part B raises the obvious next question from a competent bidder: checked against what. That makes the Platform PRD's open question on consultant disclosure sharper rather than softer, and it is better to decide it deliberately now than to answer it under pressure in a bidder clarification. The recommendation is to resolve it before Phase C, as the Platform PRD already suggests.

# 12  Open questions

| # | Question | Recommendation |
| --- | --- | --- |
| 1 | What deviation threshold triggers a flag, and who sets it? | PM team sets, AfCEN proposes. It is the PM team's noise budget, and their acceptance rate is the metric. |
| 2 | Which Part B sections and Part C benchmarks map to each of D1 to D11? | Complete from TOR Section 8.1 before the demo, if it is to show a real deliverable. |
| 3 | Is Part B published to bidders? | Developer's call. Note it needs no RFP change if issued as a PM-side standard. |
| 4 | May a low-confidence benchmark raise a Material flag? | No. Advisory at most until a metric has three or more sources. |
| 5 | Who escalates the 2020 rates to current prices before launch? | Needs an owner. Nothing in Part C is usable at a Material threshold until this is done. |
| 6 | Are the Consultant's own model files checkable at launch, or only reported figures? | Reported figures at launch. Model-file checks depend on FR-9 and FR-10 and are a Phase B question. |